Allegion helps keep people safe where they live, work and visit. With more than 25 brands sold globally we specialize in security around the doorway and beyond: everything from residential and commercial locks, door closers and exit devices, steel doors and frames, to access control and workforce productivity solutions. Access to the proper tools and resources, as well as expert consultants, can streamline the specification process.

Allegion offers specification writing services, AIA-approved training, code consulting and other services, as well as our proprietary Overtur cloud-based collaboration site, to help architects specify the right door hardware solution for every type of project.

Allegion's portfolio includes strategic brands LCN, Schlage and Von Duprin; and other brands including Dexter by Schlage, Falcon, Glynn-Johnson, ISONAS, Ives, Kryptonite, Locknetics, Steelcraft, and Zero.

# For additional information, contact:

# Allegion

# 11819 North Pennsylvania Street
	Carmel, IN 46032 USA

# Phone: +1 877 671-7011

# Web: us.allegion.com

# E-mail: info@allegion.com

SECTION 28 15 11 – INTEGRATED CREDENTIAL READERS

PART 1 GENERAL

summary

Section includes mobile enabled card readers capable of functioning with CSN cards, proximity cards, smart cards and mobile devices using NFC and Bluetooth communications.

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Divisions 26, 27, and 28 basic materials and methods sections apply to work specified in this section.

Related Sections

Division 08 Openings

08 06 71 Door Hardware Schedule

08 10 00 Doors and Frames

08 31 13.53 Security Access Doors and Frames

08 42 00 Entrances

08 74 00 Non-Integrated Access Control Hardware

Division 28 Electronic Safety and Security

28 05 11 Cyber Security Requirements for Electronic Safety and Security

28 05 31 Communications Equipment for Electronic Safety and Security

28 06 10 Schedules for Access Control

28 13 00 Access Control Software and Database Management

28 14 00 Access Control System Hardware

REFERENCES

Abbreviations and Acronyms

ASK – Amplitude Shift Keying

CSN – Card Serial Number

BLE – Bluetooth Low Energy

FSK – Frequency Shift Keying

NFC – Near Field Communications

Definitions

IP based Reader-Controller - An intelligent network-connected reader controller unit with inputs, outputs and data storage capability.

Credential - RFID based token assigned to an entity and used to identify that entity.

Mobile Credential – Token using Bluetooth® Low Energy on any Android or Apple device

CSN Card – A contactless smart card containing read-only RFID.

Identifier - A credential card, keypad personal identification number or code, or other unique identification entered as data into the entry-control database for the purpose of identifying an individual. Where this term is presented with an initial capital letter, this definition applies.

RFID - An automatic identification method, relying on storing and remotely retrieving data using devices called RFID tags or transponders.

Reference Standards

ISO 14443 - Cards and security devices for personal identification — Contactless proximity objects

ISO 15693 - Identification cards — Contactless integrated circuit cards — Vicinity cards

Underwriters' Laboratories

UL 294 V7 & cUL

FCC

IC

RED Directive

CE Mark

IP65

REACH

Bluetooth SIG

Directive 2002/95/EC Restriction of Hazardous Substances (RoHS)

SUBMITTALS

Product Data

Manufacturer’s printed or electronic data sheets

Manufacturer’s installation and operation manuals

Where applicable, SIA OSDP Verified documentation.

QUALITY ASSURANCE

Manufacturer shall be ISO 9001 certified with a minimum of three years’ experience in manufacturing low voltage power supply equipment.

Manufacturer’s products shall be manufactured in the United States of America.

DELIVERY, STORAGE, AND HANDLING

IP-based Reader-Controllers:

Store in temperature and humidity-controlled environment in original manufacturer's sealed containers. Maintain ambient temperature between -40 and 120 deg F (-40 and 50 deg C).

Open each container; verify contents against packing list, and file copy of packing list, complete with container identification for inclusion in operation and maintenance data.

Mark packing list with designations that have been assigned to materials and equipment.

COORDINATION

Security: Coordinate installation of door hardware, keying, and access control with Owner's security consultant.

warranty

Security Integrator shall provide a limited one year hardware warranty for the product to be free of defects in material and workmanship.

Manufacturer shall provide a warranty for the system to be free of defects in material and workmanship for 12 months from date of installation, not to exceed 24 months from the date of shipment from factory.

Manufacturer shall make available an extended warranty and maintenance support option.

PART 2 PRODUCTS

EQUIPMENT

Authorized Manufacturer(s): Schlage

Models:

Hardware:

IP Reader Controller

Acceptable Manufacturers: No Substitution.

DESCRIPTION

The mobile enabled multi-technology IP reader controllers shall connect to existing IT networks via a single PoE cable, make local access control decisions at the door, provide real-time connectivity to the access control system while reading CSN cards, proximity cards, smart cards, and NFC/BLE credentials from a mobile device.

HARDWARE COMPONENTS

Multi-technology IP Reader-Controller:

Manufacturer:

Schlage

RC11 mullion mount

Delete RC models not being utilized for this project.

        - Schlage RC15 single gang mount

        - Schlage RCK15 single gang mount with keypad

      - Read Technologies: The readers shall support the following technologies:

125 kHz contactless proximity cards

Compatibility: prox FSK & ASK such as Schlage® Proximity, HID® Proximity, GE/CASI® Proximity, AWID® Proximity, LenelProx®

13.56 MHz contactless smart cards

Schlage smart cards using MIFARE Classic®, Schlage smart cards using MIFARE Plus®, Schlage smart cards using MIFARE® DESFire®

Mobile Credential Model

CSN

DESFire® CSN, HID iCLASS® CSN, Inside Contactless PicoTag® CSN, ST Microelectronics® CSN, Texas Instruments Tag-It®, CSN, Phillips I-Code® CSN

2.4 GHz Bluetooth Low Energy Schlage mobile credential

13.56MHz NFC mobile credential

Keypad

The readers shall be available with the additional functionality of an integral keypad.

Intelligence capacity

64,000 credentials

5000 stored access events

32 schedules per credential

32 holidays

Input/output

Inputs

Three configurable (Default usage - door sense, request for exit/auxiliary)

Outputs

One solid state relay controlling the electric lock rated at 12 VDC @ 600 mA.

Communications Interface

Network Communications

10/100 Mbps

Half or full duplex

Ethernet

Websockets

Standard CAT5E, CAT6, or better cable

Network host or client modes

DHCP addressing

Audible communications

IP reader controller shall provide the ability to enable and disable audible indication.

Security

TLS version 1.2 encryption

Tamper detection via accelerometer

Encrypted lock control with optional module

Electrical

System Interfaces

2 TTL lines

Clock & Data

Power Voltage Range

12 VDC

PoE (IEEE802.3af, Class 0)

PoE+ (IEEE802.3at)

Operating Current – 210-225mA peak

Auxiliary Power Output – 12 VDC @ 600mA

Connection

26 AWG, CAT 5E 8” length

User

LED Indicators (3) - reader status, network connection

Programming - Microcode flash upgradeable

Dual-mode reset button - Power-cycle reader and Reset-to-Factory defaults

Physical and Environmental

Operating Temperature - -40º to +66º C

Humidity - 0 - 100%

Weather Resistance – Conformal Coated components for weather resistance

Certifications

UL-294 V7 Compliant

FCC 47 CFR Part 15

IC Certification

cUL Listed

RED Directive

CE Mark

IP65

REACH

Bluetooth SIG

RoHS 3

Enclosure

Durable U/V stabilized, flame-retardant ABS

Form Factor: Wall mount and mullion mount

Dimensions:

Mullion (5.94” x 1.77” x 1”)

Wall mount (5.13” x 3.25” x 1”)

Accessories

Provide pigtail cable to connect the reader controller to the locking device and other accessories around the door.

Provide Advanced Security Module at all reader controllers.

COMMISIONING

The Manufacturer shall have a mobile app available to commission and configure readers.

PART 3 EXECUTION

INSTALLATION

Install all equipment in accordance with the manufacturer’s installation manuals, wiring diagrams and recommendations.

Contractor personnel shall comply with all application state of local licensing requirements.

CABLING

Wiring Method: Install LAN cables using techniques, practices, and methods that are consistent with Category 5e or Category 6 rating of components and that ensure Category 5e or Category 6 performance of completed and linked signal paths, end to end.

Install cables without damaging conductors, shield, or jacket.

Boxes and enclosures containing security system components or cabling, and which are easily accessible to employees or to the public, shall be provided with a lock. Junction boxes and small device enclosures below ceiling level and easily accessible to employees or the public shall be covered with a suitable cover plate and secured with tamperproof screws.

FIELD QUALITY CONTROL

Contractor shall inspect, test, and adjust components and equipment installation.

Results shall be reported in writing.

Contractor shall remove and replace malfunctioning devices and circuits and retest as specified above.

END OF SECTION